## Sheet1
|  |  |  | Vin(min) | 85 | Volts
|  |  |  | Vin(Max) | 270 | Volts
|  |  |  | Po(max) | 440 | Watts | (this is 1/2 Horsepower(372 watts) at 85% efficiency)
|  |  |  | Vo | 350 | Volts
2.2 | Oscillator |  |  | Frequency | 500000
|  |  |  | Period | 2e-06
|  |  |  | Capacitor CT | 1.7857e-10
2.3 | ZVT Control Circuit | R12 |  |  | 1k | Ohms | This is part of the low pass filter that drives the ZVS pin. D6 needs to be selected and D13 needs to be a zener with a Max voltages of 7.5V
|  | C6 |  |  | 1000 | pF
3 | Gate Drives
3.1.1 | VRMS
4.2 | Power Stage Design
4.2.1 | Inductor Design | Peak Current |  | Ipk | 7.7059 | Amps | (assuming 95% efficiency)
|  | Inductor Current Ripple |  | I(Ripple) | 1.5412 | Amps | Assuming 20% Ripple Ratio
|  | Conversion Ratio |  | D | 0.65655 | Ratio
|  |  |  | L1 | 0.00011076 | Henries
4.2.2 | Output Capacitor Selection | Capacitor |  | Co | 0.00051084
4.2.3 | Power MOSFET & Diode Selection | MOSFET | Cree MOSFET N-CH 900V 36A TO247-3 Silicon Carbide |  |  |  | C3M0065090D | Data Sheet | C3M0065090D
|  | Diode | Cree Diode Silicon Carbide Schottky 13A (DC) Through Hole TO-220-2 Isolated Tab |  |  |  | C3D06065I | Data Sheet | C3D06065I
|  |  | Diode Reverse Recovery | trr | 0 | Seconds
4.3 | ZVT Circuit Design
4.3.1 | Resonant Inductor | Diode recovery slew rate |  | di/dt | 2825508211.3048 | A/μs | A practical Value of 1 Nano Seconds was used for diode recovery time. (SiC Diodes have no recovery time)
|  | Peak resonant inductor current |  | IINp | 8.4765 | Amps
|  | Resonant Inductor |  | Lr | 1.2387e-07 | Henries
|  | Resonant Characteristic Impedance |  |  | 32.1288
|  | Resonant Frequency |  |  | 259372328.9618
|  | Peak resonant inductor current |  |  | 18.5996
4.3.2 | Resonant Capacitance Related Equations | Resonant Capacitor |  | Cr | 120 | pF | The equivalent resonant capacitance is equal to the Coss (output capacitance) plus an additional capcitor in parallelle with the main power MOSFET
|  |  |  | t01 | 2.7273e-09 | Seconds
|  |  |  | t12 | 6.0561e-09 | Seconds
|  |  |  | Dmin | 0.0048917
|  |  |  | Vo(min) | 271.3273 | Volts
|  |  |  | tZVT | 9.0561e-09 | Seconds
|  | RMS Current of ZVT Switch |  | IRMS | 1.2516 | Amps
𝐶𝑇=1/(11200×𝑓_𝑠 )
𝐼_𝑃𝐾=(2×𝑃𝑜/𝜂)/(√2×𝑉_(𝐼𝑁(𝑚𝑖𝑛)) )
Δ𝐼_𝐿=0.2×(𝐼_𝑃𝑘)
𝐷= (𝑉_𝑂−𝑉_𝐼𝑁)/𝑉_𝑂
𝐿=(𝑉_𝐼𝑁×𝐷×𝑇_𝑆)/Δ𝐼
𝐶_𝑂=(2×𝑃_𝑂×𝑡_𝐻)/(𝑉_𝑂^2−𝑉_𝑀𝐼𝑁^2 )
𝑑𝑖/𝑑𝑡= 𝐼_𝐼𝑁𝑝/(3×𝑡_𝑟𝑟 )
I
𝐼_𝐼𝑁𝑝=𝐼_𝑝𝑘+1/2 ∆I
𝐿_𝑟= 𝑉_𝑂/((𝑑𝑖/𝑑𝑡))
𝑍_𝑛= √(𝐿_𝑟/𝐶_𝑟 )
𝜔= √(1/(𝐿_𝑟 × 𝐶_𝑟 ))
𝐼_(:_𝑟= 𝐼_𝐼𝑁 )+𝑉_𝑂/𝑍_𝑛 ×sin⁡(𝜔𝑡)